## X4 Current Data
TAG NO: |  |  | 110-GENM-01 | [5 empty] | Hookup Drawing No: | [5 empty] | Loop Wiring Diagrams: | [10 empty] | C-110-A-001 | C-110-A-001 | C-110-A-001
[9 empty] | Spec No: | [5 empty] | Vessel Number: | [6 empty] | Electrical Protection Method | Gas / Dust Groups | Temperature Category |  | C-110-A-002 | C-110-A-002 | C-110-A-002
Asset No: | [8 empty] | P&ID: |  | Selected Diagram |  |  |  | Line ID: |  |  |  |  | Size: | Schedule: |  |  |  |  | C-110-A-003 | C-110-A-003 | C-110-A-003
Service Description: | [14 empty] | Manufacturer: |  |  | VAISALA |  |  |  | EEx o | IIC | T1 |  | C-110-A-004 | C-110-A-004 | C-110-A-004
[15 empty] | Model: |  | WXT530 Series |  |  |  |  | EEx p | IIC | T2 |  | C-110-AIT-1001A | C-110-AIT-1001A | C-110-AIT-1001A
P.O. Number: | [12 empty] | User 1: | [8 empty] | EEx q | IIB | T2A |  | C-110-AIT-1001B | C-110-AIT-1001B | C-110-AIT-1001B
REQ. Number: | [12 empty] | User 2: | [8 empty] | EEx d | IIA | T2B |  | C-110-AIT-1002A | C-110-AIT-1002A | C-110-AIT-1002A
GENERAL | [21 empty] | EEx e | I | T2C |  | C-110-AIT-1002B | C-110-AIT-1002B | C-110-AIT-1002B
| Area Classification: | [20 empty] | EEx ia | N/A | T2D |  | C-110-FD-1001A | C-110-FD-1001A | C-110-FD-1001A
| Ambient Relative Humidity: | [20 empty] | EEx ib |  | T3 |  | C-110-FD-1001B | C-110-FD-1001B | C-110-FD-1001B
| Ambient Temperature: | [20 empty] | EEx n | Certification | T3A |  | C-110-FD-1001C | C-110-FD-1001C | C-110-FD-1001C
| Activation Source(s): | [20 empty] | EEx m |  | T3B |  | C-110-FH-001 | C-110-FH-001 | C-110-FH-001
| Function: | [20 empty] | EEx s | BASEEFA Eexd IIB T4 & T5 | T3C |  | C-110-FH-002 | C-110-FH-002 | C-110-FH-002
[22 empty] | N/A | ATEX | T4 |  | C-110-H-001 | C-110-H-001 | C-110-H-001
WEATHER STATION | [22 empty] | CENELEC EN50014 and EN50018 | T4A |  | C-110-H-003 | C-110-H-003 | C-110-H-003
| POWER | Power Requirements: |  |  |  | 24 VDC | [6 empty] | PRESS. | Range: |  |  | 600 ... 1100 hPa | [5 empty] | UL Listed: Class 1, Zone 1 & 2, AExd IIB T4 & T5 | T5 |  | C-110-H-010 | C-110-H-010 | C-110-H-010
|  | Power Consumption: |  |  |  | 3.5 mA @ 12VDC | [7 empty] | Accuracy: |  |  | ±0.5 hPa at 0 … +30 °C / ±1 hPa at -52 … +60 °C | [5 empty] | N/A | T6 |  | C-110-H-013 | C-110-H-013 | C-110-H-013
|  | Current Consumption: |  |  |  | Max. 15 mA | [7 empty] | Resolution: |  |  | 0.1 hPa / 10 Pa / 0.001 bar | [6 empty] | N/A |  | C-110-H-014 | C-110-H-014 | C-110-H-014
|  | Reverse Polarity: | [10 empty] | TEMP. | Range: |  |  | -52 ... +60 °C | [8 empty] | C-110-H-015 | C-110-H-015 | C-110-H-015
| WIND SPEED | Wind Speed: |  |  |  | 0 ... 60 m/s (134 mph) | [7 empty] | Accuracy: |  |  | ±0.3 °C | [8 empty] | C-110-H-016 | C-110-H-016 | C-110-H-016
|  | Response Time: |  |  |  | 0.25 s | [7 empty] | Resolution: |  |  | 0.1 °C |  |  |  |  | Power | Lens Colour |  |  | C-110-H-017 | C-110-H-017 | C-110-H-017
|  | Variables: |  |  |  | Average, maximum, and minimum | [6 empty] | HUMID. | Range: |  |  | 0 ... 100 %RH | [8 empty] | C-110-H-020 | C-110-H-020 | C-110-H-020
|  | Accuracy: |  |  |  | ±3 % at 10 m/s (22 mph) | [7 empty] | Accuracy: |  |  | ±3 %RH at 0 ... 90 %RH / ±5 %RH at 90 ... 100 %RH | [8 empty] | C-110-H-021 | C-110-H-021 | C-110-H-021
|  | Resolution: |  |  |  | 0.1 m/s (km/h, mph, knots) | [7 empty] | Resolution: |  |  | 0.1 %RH |  |  |  |  | 24 VDC | Red |  |  | C-110-H-022 | C-110-H-022 | C-110-H-022
| WIND DIR. | Azimuth: |  |  |  | 0 ... 360° | [6 empty] | HEATER | Heating: |  |  | Options: DC, AC, full-wave rectified AC |  |  |  |  | ~110 VAC 50/60Hz | Blue |  |  | C-110-H-023 | C-110-H-023 | C-110-H-023
|  | Response Time: |  |  |  | 0.25 s | [7 empty] | Voltage: |  |  | 12 ... 24 VDC |  |  |  |  | ~240 VAC 50/60Hz | Amber |  |  | C-110-H-024 | C-110-H-024 | C-110-H-024
|  | Variables: |  |  |  | Average, maximum, and minimum | [7 empty] | Current: |  |  | 12 ... 17 VACrms |  |  |  |  | N/A | Green |  |  | C-110-HS-1010 | C-110-HS-1010 | C-110-HS-1010
|  | Accuracy: |  |  |  | ±3.0° at 10 m/s (22 mph) | [6 empty] | COM | Hardware Layer: |  |  | SDI-12, RS-232, RS-485, RS-422 | [5 empty] | Yellow |  |  | C-110-LIT-072 | C-110-LIT-072 | C-110-LIT-072
|  | Resolution: |  |  |  | 1° | [7 empty] | Protocols: |  |  | SDI-12 v1.3 / ASCII / NMEA 0183 v3.0 / Modbus | [5 empty] | Clear |  |  | C-110-LIT-1001 | C-110-LIT-1001 | C-110-LIT-1001
| PRECIPITATION | Rainfall: |  |  |  | Cumulative accumulation | [6 empty] | AI | Solar Radiation: |  |  | Kipp & Zonen CMP3 | [8 empty] | C-110-LIT-1102 | C-110-LIT-1102 | C-110-LIT-1102
|  | Collecting Area: |  |  |  | 60 cm2 (9.3 in2) | [7 empty] | Level Measurement: |  |  | IRU-9429 | [8 empty] | C-110-PD-001 | C-110-PD-001 | C-110-PD-001
|  | Resolution: |  |  |  | 0.01 mm (0.001 in) | [7 empty] | Rain Gauge: |  |  | Vaisala Rain Gauge RG13 |  |  |  |  | Enclosure Protection IP Rating |  |  |  | C-110-PD-002 | C-110-PD-002 | C-110-PD-002
|  | Rain Duration: |  |  |  | Counting each 10‑second increment | [7 empty] | Temperature: |  |  | PT1000 |  |  |  |  | First Number - Protection against solids ingress | Second Number - Protection against water ingress |  |  | C-110-PD-003 | C-110-PD-003 | C-110-PD-003
|  | Resolution: |  |  |  | 10 s | [6 empty] | AO | Wind Speed: |  |  | 0 … 20 mA or 4 … 20 mA |  |  |  |  | 0 | 0 |  |  | C-110-PD-004 | C-110-PD-004 | C-110-PD-004
|  | Rain Intensity: |  |  |  | Running 1-minute average in 10 s steps | [7 empty] | Wind Direction: |  |  | 0 … 20 mA or 4 … 20 mA |  |  |  |  | 1 | 1 |  |  | C-110-PD-005 | C-110-PD-005 | C-110-PD-005
|  | Range: |  |  |  | 0 ... 200 mm/h (0 ... 7.87 in/h) | [7 empty] | Load Impedance: |  |  | Max. 200 Ω |  |  |  |  | 2 | 2 |  |  | C-110-PD-006 | C-110-PD-006 | C-110-PD-006
|  | Resolution: |  |  |  | 0.1 mm/h (0.01 in/h) | [6 empty] | GENERAL | Housing IP Rating |  |  | Without mounting kit: IP65 / With mounting kit: IP66 |  |  |  |  | 3 | 3 |  |  | C-110-PD-007 | C-110-PD-007 | C-110-PD-007
|  | Hail: |  |  |  | Cumulative amount of hits | [7 empty] | Storage Temperature: |  |  | -60 … +70 °C (-76 … +158 °F) |  |  |  |  | 4 | 4 |  |  | C-110-PD-008 | C-110-PD-008 | C-110-PD-008
|  | Resolution: |  |  |  | 0.1 hits/cm2 (1 hits/in2), 1 hit | [7 empty] | Operating Temperature: |  |  | -52 … +60 °C (-60 … +140 °F) |  |  |  |  | 5 | 5 |  |  | C-110-PD-009 | C-110-PD-009 | C-110-PD-009
|  | Hail Duration: |  |  |  | Counting each 10‑second increment | [7 empty] | Relative Humidity: |  |  | 0 … 100 %RH |  |  |  |  | 6 | 6 |  |  | C-110-PD-010 | C-110-PD-010 | C-110-PD-010
|  | Resolution: |  |  |  | 0.1 hits/cm2 (1 hits/in2), 1 hit | [7 empty] | Pressure: |  |  | 600 … 1100 hPa | [8 empty] | C-110-PD-011 | C-110-PD-011
|  | Hail Intensity: |  |  |  | 1-minute running average | [7 empty] | Wind: |  |  | 0 … 60 m/s (0 … 134 mph) | [8 empty] | C-110-PD-012 | C-110-PD-012
|  | Resolution: |  |  |  | 0.1 hits/cm2h (1 hits/in2h), 1 hit/h | [15 empty] | N/A | 7 |  |  | C-110-PD-020 | C-110-PD-020 | C-110-PD-011
| Connection 1: | [11 empty] | Connection 2: | [12 empty] | C-110-PD-021 | C-110-PD-021
| Electrical Protection: | [6 empty] | Gas Group: |  |  |  | Temperature Category: |  |  |  | Enclosure Protection IP Rating: | [6 empty] | 8 |  |  | C-110-PD-022 | C-110-PD-022 | C-110-PD-012
NOTES | [21 empty] | ENCLOSURE PROTECTION: | N/A |  |  | C-110-PD-023 | C-110-PD-023 | C-110-PD-020
[22 empty] | IP20 |  |  |  | C-110-PD-024 | C-110-PD-024 | C-110-PD-021
[22 empty] | IP40 |  |  |  | C-110-PD-025 | C-110-PD-025 | C-110-PD-022
[22 empty] | IP54 |  |  |  | C-110-PD-026 | C-110-PD-026 | C-110-PD-023
[22 empty] | IP56 |  |  |  | C-110-PD-027 | C-110-PD-027 | C-110-PD-024
[22 empty] | IP65 |  |  |  | C-110-PD-030 | C-110-PD-030 | C-110-PD-025
[22 empty] | IP66 |  |  |  | C-110-PD-031 | C-110-PD-031 | C-110-PD-026
[22 empty] | IP67 |  |  |  | C-110-PD-040A | C-110-PD-040A | C-110-PD-027
[22 empty] | IP68 |  |  |  | C-110-PD-040B | C-110-PD-040B | C-110-PD-030
| ATEX REGISTER | [20 empty] | See Notes |  |  |  | C-110-PD-041A | C-110-PD-041A | C-110-PD-031
| EC Type Examination Cert. | [11 empty] | NOBO REF NUMBER |  |  |  | DNVG CERTIFICATE No. TAA00000VF | [8 empty] | C-110-PD-041B | C-110-PD-041B | C-110-PD-040A
| EC Declaration of Conformity | [11 empty] | User 3: | [12 empty] | C-110-PD-045 | C-110-PD-045 | C-110-PD-040B
| Production QA Notification | [11 empty] | User 4: | [12 empty] | C-110-PD-046 | C-110-PD-046 | C-110-PD-041A
| Prod. QA Not. Validity Date | [11 empty] | User 5: | [12 empty] | C-110-PD-047 | C-110-PD-047 | C-110-PD-041B
User 6 | [12 empty] | User 8 | [12 empty] | C-110-PD-048 | C-110-PD-048 | C-110-PD-045
User 7 | [12 empty] | User 9 | [12 empty] | C-110-PD-049 | C-110-PD-049 | C-110-PD-046
[26 empty] | C-110-PD-050 | C-110-PD-050 | C-110-PD-047
[14 empty] | INSTRUMENT SPECIFICATION | [11 empty] | C-110-PD-051 | C-110-PD-051 | C-110-PD-048
[14 empty] | Weatherstation | [11 empty] | C-110-PD-052 | C-110-PD-052 | C-110-PD-049
[26 empty] | C-110-PD-053 | C-110-PD-053 | C-110-PD-050
[26 empty] | C-110-PD-055 | C-110-PD-055 | C-110-PD-051
[14 empty] | Project : |  |  |  |  | Sheet | [6 empty] | C-110-PD-056 | C-110-PD-056 | C-110-PD-052
[14 empty] | Project No.: |  |  |  |  | BES Dwg: | [6 empty] | C-110-PD-057 | C-110-PD-057 | C-110-PD-053
REV |  | By |  | Chk | App |  | Date |  |  | Revision Description |  |  |  | Form No. DS_BES_Weatherstation |  |  |  |  | Client Dwg | [6 empty] | C-110-PD-058 | C-110-PD-058 | C-110-PD-055
[19 empty] | 2021-07-27 07:31 | [6 empty] | C-110-PD-059 | C-110-PD-059 | C-110-PD-056
[26 empty] | C-110-PD-060 | C-110-PD-060 | C-110-PD-057
[26 empty] | C-110-PD-061 | C-110-PD-061 | C-110-PD-058
[26 empty] | C-110-PD-062 | C-110-PD-062 | C-110-PD-059
[26 empty] | C-110-PD-063 | C-110-PD-063 | C-110-PD-060
[26 empty] | C-110-PD-064 | C-110-PD-064 | C-110-PD-061
[26 empty] | C-110-PD-065 | C-110-PD-065 | C-110-PD-062
[26 empty] | C-110-PD-070 | C-110-PD-070 | C-110-PD-063
[26 empty] | C-110-PD-071A/D | C-110-PD-071A/D | C-110-PD-064
[26 empty] | C-110-PD-072A/D | C-110-PD-072A/D | C-110-PD-065
[26 empty] | C-110-PD-073A/D | C-110-PD-073A/D | C-110-PD-070
[26 empty] | C-110-PD-074A/D | C-110-PD-074A/D | C-110-PD-071A/D
[26 empty] | C-110-PIT-074 | C-110-PIT-074 | C-110-PD-072A/D
[26 empty] | C-110-PIT-1001A | C-110-PIT-1001A | C-110-PD-073A/D
[26 empty] | C-110-PIT-1001B | C-110-PIT-1001B | C-110-PD-074A/D
[26 empty] | C-110-PIT-1002A | C-110-PIT-1002A | C-110-PIT-074
[26 empty] | C-110-PIT-1002B | C-110-PIT-1002B | C-110-PIT-1001A
[26 empty] | C-110-PIT-1102 | C-110-PIT-1102 | C-110-PIT-1001B
[26 empty] | C-110-PIT-1103 | C-110-PIT-1103 | C-110-PIT-1002A
[26 empty] | C-110-SOV-1001A | C-110-SOV-1001A | C-110-PIT-1002B
[26 empty] | C-110-SOV-1001B | C-110-SOV-1001B | C-110-PIT-1102
[26 empty] | C-110-SOV-1003-C | C-110-SOV-1003-C | C-110-PIT-1103
[26 empty] | C-110-SOV-1003-O | C-110-SOV-1003-O | C-110-SOV-1001A
[26 empty] | C-110-TI-1002 | C-110-TI-1002 | C-110-SOV-1001B
[26 empty] | C-110-TIT-001 | C-110-TIT-001 | C-110-SOV-1003-C
[26 empty] | C-110-TIT-1001A | C-110-TIT-1001A | C-110-SOV-1003-O
[26 empty] | C-110-TIT-1001B | C-110-TIT-1001B | C-110-TI-1002
[26 empty] | C-110-WT-1001A1 | C-110-WT-1001A1 | C-110-TIT-001
[26 empty] | C-110-WT-1001B1 | C-110-WT-1001B1 | C-110-TIT-1001A
[26 empty] | C-110-ZS-1001A | C-110-ZS-1001A | C-110-TIT-1001B
[26 empty] | C-110-ZS-1001B | C-110-ZS-1001B | C-110-WT-1001A1
[26 empty] | C-110-ZS-1002 | C-110-ZS-1002 | C-110-WT-1001B1
[26 empty] | C-110-ZSC-1001A | C-110-ZSC-1001A | C-110-ZS-1001A
[26 empty] | C-110-ZSC-1001B | C-110-ZSC-1001B | C-110-ZS-1001B
[26 empty] | C-110-ZSC-1003 | C-110-ZSC-1003 | C-110-ZS-1002
[26 empty] | C-110-ZSL-1010A | C-110-ZSL-1010A | C-110-ZSC-1001A
[25 empty] | App | C-110-ZSL-1010B | C-110-ZSL-1010B | C-110-ZSC-1001B
[25 empty] | Chk | C-110-ZSL-1010C | C-110-ZSL-1010C | C-110-ZSC-1003
[25 empty] | CurrentData | C-110-ZSO-1001A | C-110-ZSO-1001A | C-110-ZSL-1010A
[25 empty] | PreviousData | C-110-ZSO-1001B | C-110-ZSO-1001B | C-110-ZSL-1010B
[25 empty] | Print_Area | C-110-ZSO-1003 | C-110-ZSO-1003 | C-110-ZSL-1010C
[25 empty] | Rev | C-110-ZSO-1001B |  | C-110-ZSO-1001A
[25 empty] | RevBy | C-110-ZSO-1003 |  | C-110-ZSO-1001B
[25 empty] | RevDate |  |  | C-110-ZSO-1003
RevList
RevStatus
WSTempResolution
WSWindSpeedAccuracy
Service:
Critical:
rev
rev
rev
rev
Note on G46: Protection Method EEx o - Oil Immersion (zone 1, 2) EEx p - Pressurization (zone 1, 2) EEx q - Powder Filling (zone 1, 2) EEx d - Flameproofing (Explosion Proof) (zone 1, 2) EEx e - Increased Safety (zone 1, 2) EEx ia - Intrinsic Safety (zone 0, 1, 2) EEx ib - Intrinsic Safety (zone 1, 2) EEx n - Non-Incedive (zone 1, 2) EEx m - Encapsulation (zone 1, 2) EEx s - Special Protection (zone 0, 1, 2)
Note on M46: Gas / Dust Groups IIC - Acetylene IIC - Hydrogen IIB - Ethylene IIA - Propane I - Methane
Note on T46: Temperature Category T1 - 450 oC T2 - 300 oC T2A - 280 oC T2B - 260 oC T2C - 230 oC T2D - 215 oC T3 - 200 oC T3A - 180 oC T3B - 165 oC T3C - 160 oC T4 - 135 oC T4A - 120 oC T5 - 100 oC T6 - 85 oC
Note on AD46: Protection against solids ingress. 0 - No protection against live or moving parts. 1 - Protection against contact by large surfaces. 2 - Protection against contact by fingers. 3 - Protection against contact by tools, wires objects > 2.5mm. 4 - Protection against contact by tools, wires objects > 1.0mm. 5 - Complete protection against contact. Ingress of dust not in harmful quantities. 6 - Complete protection against contact. Protection against Ingress of dust. Protection against water ingress. 0 - No protection. 1 - Protection against drops of condensed water. 2 - Protection against liquid drops at 15o from vertical. 3 - Protection against liquid drops at 60o from vertical. 4 - Protection against spashing from any direction. 5 - Protection against water jets from any direction under stated conditions. 6 - Protection against heavy sea water under stated conditions. 7 - Protection against water immersion under stated conditions of pressure and time. 8 - Protection against indefinite immersion in water under specified pressure.